## Introduction
Calculation Tool for Mechanical, Electric and Plumbing Life Cycle Assessment
Developed by the Carbon Leadership Forum, University of Washington
Funded by the Oregon Department of Environmental Quality
January | 2019
Tab descriptions:
| Tab name | Description of contents
| Introduction | Provides an overview of this spreadsheet file (this tab)
| Custom quantities input | The user can enter custom quantities on this tab and produce numerical results. For data input fill 'Midpoint of material quantity estimate (calculated) [kg/m2]'
| Source data | Contains background information on the LCA data used for the MEP items
| Results | Contains graphs of the results from the "Custom quantities input" tab. Note that the colors between the pie charts and bar charts do not correspond.
Impacts assessed
| GWP | Global warming potential
Other abbreviations:
| Abbreviation | Definition
| m2 | square meter
| occ | occupant
| QTO | quantity take-off
| CO2eq | carbon dioxide equivalent
| SO2eq | sulfur dioxide equivalent
| Neq | nitrogen equivalent
| CFC11eq | chlorofluorocarbon-11 equivalent
| O3eq | ozone equivalent
| MJ | megajoules
| kg | kilograms
| Abbreviation | Definition
| m2 | square meter
| occ | occupant
| QTO | quantity take-off
| CO2eq | carbon dioxide equivalent
| SO2eq | sulfur dioxide equivalent
| Neq | nitrogen equivalent
| CFC11eq | chlorofluorocarbon-11 equivalent
| O3eq | ozone equivalent
| MJ | megajoules
| kg | kilograms

## Source Data
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
Product short name | Product full name | Type | Sub Products included | Manufacturer | Type of source | Program | Country | Region | Issue date | Valid date | Declared/ Functional Unit | Model | Operational Weight (kg) | kg of material per declared unit | Total GWP [kg CO2-eq.]
Non-metallic boxes | Solvent Weld Soil and Waste Pipe | electrical | NA | NA | Database | QUARTZ | USA | Northamerica | 2014 | 2019 | 1kg |  |  |  | 3.19
| LEDline System | electrical | NA | Phillipps | EPD | International EPD System | Germany | Europe | 2014 | 2019 | 1 Xitanium driver + 4 Fortimo LEDLines |  |  |  | 41.2
LED fixtures | Hublots LED Chartres Essentiel ON/OFF | electrical |  | Sarlam | EPD | PEP | France | France | 2017 | 2022 | Assurer un éclairage général de 1000 lumens sous 230 V pendant 10 ans, à l’intérieur comme à l’extérieur, des zones de circulations, des locaux à usage tertiaire et d’habitation. Tenue au choc IK 10, étanchéité IP 55 et une tenue au feu de 650 °C / 30 s. |  | 1.804 | 1.084 | 11.3
Fixtures | Fluorescent lamp T8-18W; 1 piece (en | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | Fluorescent lamp - tubelight T8/T26 18W - 1.0 pcs |  |  |  | 0.3523
Battery 20W Unit | Lithium iron phosphate (LiFePO4) battery (per 1kWh storage); 1kWh storage capacity (en) | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | 23.3 kg/Stk |  |  |  | 11.6522
Battery | Lithium iron phosphate (LiFePO4) battery (per 1kWh storage); 1kWh storage capacity (en) | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | 23.3 kg/Stk |  |  |  | 11.6522
Occupancy sensors | Wattstopper® - Dual Technology Wall Switch Occupancy Sensors | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | 1 unit |  |  |  | 4.5
Daylight sensors | Wattstopper® - Dual Technology Wall Switch Occupancy Sensors | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | 1 unit |  |  |  | 4.5
MC Cable (metallic cable) | Cable 1-wire; 1 piece 1.0 m (Length), 0.02 kg/m (linear density) | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | 1 m |  |  |  | 0.08631
Copper feeders | Cable 1-wire; 1 piece 1.0 m (Length), 0.02 kg/m (linear density) | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | 1 m |  |  |  | 0.08631
Metal boxes | Cable 1-wire; 1 piece 1.0 m (Length), 0.02 kg/m (linear density) | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | 1 m |  |  |  | 0.08631
Code minimum time clock, 0.68 lbs/EA | Cable 1-wire; 1 piece 1.0 m (Length), 0.02 kg/m (linear density) | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | 1 m |  |  |  | 0.08631
Data/WAP (Wireless) | Cable 1-wire; 1 piece 1.0 m (Length), 0.02 kg/m (linear density) | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | 1 m |  |  |  | 0.08631
Feeder Wire | Cable 1-wire; 1 piece 1.0 m (Length), 0.02 kg/m (linear density) | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | 1 m |  |  |  | 0.08631
Aluminum feeders 100amp and over | Cable 1-wire; 1 piece 1.0 m (Length), 0.02 kg/m (linear density) | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | 1 m |  |  |  | 0.08631
FA | Cable 1-wire; 1 piece 1.0 m (Length), 0.02 kg/m (linear density) | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | 1 m |  |  |  | 0.08631
Basic Service Switchgear | Rocker lightswitch; 1 piece | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | Light switch (piece) - 1.0 pcs. (Number of pieces) |  |  | 30 | 0.5181
D-Rings 0.15 lbs/EA | Rocker lightswitch; 1 piece | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | Light switch (piece) - 1.0 pcs. (Number of pieces) |  |  | 30 | 0.5181
Transformer | Rocker lightswitch; 1 piece | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | Light switch (piece) - 1.0 pcs. (Number of pieces) |  |  | 30 | 0.5181
Transformer Vault | Rocker lightswitch; 1 piece | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | Light switch (piece) - 1.0 pcs. (Number of pieces) |  |  | 30 | 0.5181
Backup Generator | Rocker lightswitch; 1 piece | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | Light switch (piece) - 1.0 pcs. (Number of pieces) |  |  | 30 | 0.5181
Non-Metallic Cable | Cable CAT 7; 1 piece (en) | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | 1.0 m (Length), 0.0589 kg/m |  |  |  | 0.2935
EMT Conduit | Steel Conduit/ Electric Rigid Steel Conduit | electrical | NA | NA | Database | QUARTZ | USA | Northamerica | 2014 | 2019 | 1kg |  |  |  | 2.82
Energy meters, 0.59 lbs/EA | Wattstopper® - Digital Light Management Room Controller with 0-10V Dimming | electrical | NA | Legrand | EPD | PEP | France | Europe |  |  | 1kg |  |  |  | 13
DATA/AV/Access CNTRL | Electronic control gear; 1 piece (en) en de | electrical | NA | NA | Database | Oekobaudat | Germany | Europe | 2016 | 2019 | Electronic ballast EB (piece) - 1.0 pcs. (Number of pieces) |  |  |  | 6.32
Galv sheet metal | Galvanized Steel Ducts | HVAC | NA | NA | Database | QUARTZ | USA | Northamerica | 2014 | 2019 | 1kg |  |  |  | 2.4
| Air Ventilation Duct (zinc coated steel plate) | HVAC | NA | NA | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | 1kg |  |  |  | 1.4849
| Metal circular Conduit | HVAC | NA | NA | EPD | PEP | France | France | 2018 | 2023 | Ensure the transfer of air via 1 linear m of air duct diameter 160 mm, during the life of the product 30 years old |  | 4.6 |  | 15.44
Copper pipe | Copper Piping | HVAC | NA | NA | Database | QUARTZ | USA | Northamerica | 2014 | 2019 | 1kg |  |  |  | 2.19
Cast iron pipe | Cast Iron Pipes | Plumbing | NA | NA | Database | QUARTZ | USA | Northamerica | 2014 | 2019 | 1kg |  |  |  | 2.88
PEX water pipe | PEX Water Pipe | Plumbing | NA | NA | Database | QUARTZ | USA | Northamerica | 2014 | 2019 | 1kg |  |  |  | 4.81
PVC | Solvent Weld Soil and Waste Pipe | Plumbing | NA | NA | Database | QUARTZ | USA | Northamerica | 2014 | 2019 | 1kg |  |  |  | 3.19
Stainless Steel | Steel Pipe | HVAC | NA | NA | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | 1kg |  |  |  | 2.256
| Fiber Glass Board Insulation | Insulation | NA | NA | Database | QUARTZ | USA | Northamerica |  |  | 1kg |  |  |  | 3.19
| Aluminum Cold-Rolled Sheet and plate | HVAC | NA | Industry Average | EPD | UL | USA | Northamerica |  |  | 1t | CML 2001 |  |  | 5330
Flexible duct | Aluminum Cold-Rolled Sheet and plate (functional unit converted from 1 ton to 1 kg) | HVAC | NA | Industry average | EPD | UL | USA | Northamerica | 0 | 0 | 1kg | CML 2001 |  |  | 5.33
Steel Pipe | Steel Pipe | HVAC | NA | NA | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | 1kg |  |  |  | 2.256
| Polybutadiene pipe (PB) | HVAC | NA | NA | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | 1kg |  |  |  | 4.63
| Electric heat pump (air-water) 10 kW; 1 piece (315lb) | HVAC | NA | NA | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | 1unit (315 lb or 143kg) |  | 144 |  | 449.3
Packaged units | Electric heat pump (air-water) 10 kW; 1 piece (315lb) | HVAC | NA | NA | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | 1kg | 0 | 144 |  | 3.142
| Gas condensing boiler120-400 kW (upright unit); 1 piece | HVAC | NA | NA | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | Gas condensing boiler 120-400 kW (upright unit) pieces (283 kg) |  | 283 |  | 3439
Boiler | Gas condensing boiler120-400 kW (upright unit); 1 piece | HVAC | NA | NA | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | 1 kg | 0 | 283 |  | 12.1519
Original Data | Electric heat pump (water-water) 10 kW; 1 piece (en | HVAC | NA | NA | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | Electric heat pump (Water-Water) 10 kW - 1.0 pcs. (Number of pieces) |  | 144 |  | 275.3
Pumps | Electric heat pump (water-water) 10 kW; 1 piece (en | HVAC | NA | NA | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | 1 kg | 0 | 144 |  | 1.9118
Distributed zone WSHP | Electric heat pump (water-water) 10 kW; 1 piece (en | HVAC | NA | NA | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | 1 kg | 0 | 144 |  | 1.9118
Original Data | Ventilation centralized per 10000 m3/h, 168kg. | HVAC | NA | NA | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | Ventilation centralized per 5000 m3/h - 1.0 pcs. (Number of pieces) (assume 143 kg) | NA | 168 | 168 | 339.4
Original Data | Ventilation centralized per 30000 m3/h, 168kg. | HVAC | NA | NA | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | Ventilation centralized per 5000 m3/h - 1.0 pcs. (Number of pieces) (assume 143 kg) | NA | 168 | 168 | 837.7
Cooling Tower | Ventilation centralized per 30000 m3/h, 168kg. | [11 empty] | 168 | 168 | 4.9863
DOAS ERV w/ Electric Heat | Ventilation centralized per 30000 m3/h, 168kg. | [13 empty] | 4.9863
| Ventilation centralized with heat recovery per 10000 m3/h; 1 piece, 704kg | 0 | 0 | 0 | Database | Oekobaudat | Germany | Germany | 2016 | 2019 | Ventilation centralized per 5000 m3/h - 1.0 pcs. (Number of pieces) (assume 143 kg) | NA | 704 | 704 | 2695
DOAS w/ Heat Recovery | Ventilation centralized with heat recovery per 10000 m3/h; 1 piece, 704kg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ventilation centralized per 5000 m3/h - 1.0 pcs. (Number of pieces) (assume 143 kg) | NA | 704 | 704 | 3.8281
VRF Outdoor Units | Ventilation centralized with heat recovery per 10000 m3/h; 1 piece, 704kg | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Ventilation centralized per 5000 m3/h - 1.0 pcs. (Number of pieces) (assume 143 kg) | NA | 704 | 704 | 3.8281
| Caisson de ventilation simple flux collective ou tertiaire, ou tourelle ou ventilateur CRITAIR EC | HVAC | NA | Atlantic | EPD | PEP | France | France | 2016 | 2021 | Provide an air transfer of 1 m3 / h, for ventilation, and / or air treatment and, and / or smoke extraction, and / or filtration of a building during the typical 17 year life | NA | 35.72 |  | 97000
| Caisson de ventilation simple flux collective ou tertiaire | HVAC | NA | Airvent | EPD | PEP | France | France | 2016 | 2021 | Provide an air transfer of 1 m3 / h, for ventilation, and / or air treatment and, and / or smoke extraction and / or filtration of a building during the typical service life of 17 years | AIRVENT PA 1500 / 2000 | 37 | 0.01406 | 151.96
Single Duct VAVs or CAVs | Caisson de ventilation simple flux collective ou tertiaire | HVAC | NA | Airvent | EPD | PEP | France | France | 2016 | 2021 | Provide an air transfer of 1 m3 / h, for ventilation, and / or air treatment and, and / or smoke extraction and / or filtration of a building during the typical service life of 17 years | AIRVENT PA 1500 / 2000 | 37 | 0.01406 | 4.107
VAV Terminals w/ Electric Heat | Caisson de ventilation simple flux collective ou tertiaire | HVAC | NA | Airvent | EPD | PEP | France | France | 2016 | 2021 | Provide an air transfer of 1 m3 / h, for ventilation, and / or air treatment and, and / or smoke extraction and / or filtration of a building during the typical service life of 17 years | AIRVENT PA 1500 / 2000 | 37 | 0.01406 | 4.107
VRF casettes | Caisson de ventilation simple flux collective ou tertiaire | HVAC | NA | Airvent | EPD | PEP | France | France | 2016 | 2021 | Provide an air transfer of 1 m3 / h, for ventilation, and / or air treatment and, and / or smoke extraction and / or filtration of a building during the typical service life of 17 years | AIRVENT PA 1500 / 2000 | 37 | 0.01406 | 4.107
VRF Fan Coils | Caisson de ventilation simple flux collective ou tertiaire | HVAC | NA | Airvent | EPD | PEP | France | France | 2016 | 2021 | Provide an air transfer of 1 m3 / h, for ventilation, and / or air treatment and, and / or smoke extraction and / or filtration of a building during the typical service life of 17 years | AIRVENT PA 1500 / 2000 | 37 | 0.01406 | 4.107
| Bidirectional ventilation unit for tertiary buildings | HVAC | AHU | ALDES Aéraulique - CALADAIR - FRANCE AIR - ZEHNDER Group - UNICLIMA | EPD | PEP | France | France | 2018 | 2023 | Transfer 1 m3 of air per hour for the ventilation of a building over the reference lifetime of 17 years |  | 550 | 550 | 3736
VAV AHU w/ DX | Bidirectional ventilation unit for tertiary buildings | HVAC | AHU | ALDES Aéraulique - CALADAIR - FRANCE AIR - ZEHNDER Group - UNICLIMA | EPD | PEP | France | France | 2018 | 2023 | Transfer 1 m3 of air per hour for the ventilation of a building over the reference lifetime of 17 years | 0 | 550 | 550 | 6.7927
| Air Handling Units | HVAC | Normal AHU | NA | Journal Article |  | FINLAND | Europe | 2004 | NA |  |  |  |  | 2400
| Air Handling Units | HVAC | Small AHU | NA | Journal Article |  | FINLAND | Europe | 2005 | NA | 2m3/s (4200 cfm) outdoor ventilation |  |  |  | 2000
| Air Handling Units | HVAC | Normal AHU (plate) | NA | Journal Article |  | FINLAND | Europe | 2004 | NA | 2m3/s (4200 cfm) outdoor ventilation |  |  |  | 2400
| Air Handling Units | HVAC | Small AHU (plate) | NA | Journal Article |  | FINLAND | Europe | 2005 | NA | 2m3/s (4200 cfm) outdoor ventilation |  |  |  | 2000
| Air Handling Units | HVAC | Normal AHU (wheel) | NA | Journal Article |  | FINLAND | Europe | 2006 | NA | 2m3/s (4200 cfm) outdoor ventilation |  |  |  | 1600
| Air Handling Units | HVAC | Small AHU (wheel) | NA | Journal Article |  | FINLAND | Europe | 2007 | NA | 2m3/s (4200 cfm) outdoor ventilation |  |  |  | 1200
AHU French | Caisson de ventilation simple flux collective ou tertiaire | HVAC |  |  |  | PEP |  |  |  |  | Assurer un transfert d'air d'1 m3/h, en vue de la ventilation, et / ou traitement d'air et, et / ou désenfumage, et / ou filtration d'un bâtiment pendant la durée de vie typique de 17 ans |  |  |  | 291
Chiller | CENTRAVAC CHILLER PORTAFOLIO | HVAC | Trane® CenTraVac™ chiller (models CVHE, CVHF, CVHG, CDHF, CDHG) | Trane® | EPD | UL Environment | USA | Northamerica | 2015 | 2019 | One ton of cooling capacity “one ton of cooling capacity” based on an average case 1,840-ton centrifugal chiller mode | TRACI 2.1 | 35894 | 13.6397 | 121.09
Air Cooled Chiller or Water Cooled Chiller + Cooling Tower | CENTRAVAC CHILLER PORTAFOLIO | HVAC | Trane® CenTraVac™ chiller (models CVHE, CVHF, CVHG, CDHF, CDHG) | Trane® | EPD | UL Environment | USA | Northamerica | 2015 | 2019 | One ton of cooling capacity “one ton of cooling capacity” based on an average case 1,840-ton centrifugal chiller mode (300 kgs) | TRACI 2.1 | 35894 | 13.6397 | 8.8777
Refrigerants | R-410A | Refrigerants |  | NA | GBRS | LEED | USA | Northamerica | 2013 | 2019 | kg |  |  |  | 1890
Insulation - duct wrap | Armaflex® Class 1 | insulation |  | Armacell Asia Ltd | EPD | UL | USA | Northamerica | 2015 | 2020 | 1 kg of insulation material without facing with a building service life of 60 years. | CML |  |  | 5.69
| Earthwool® 1000° Pipe Insulation | insulation |  | Knauf Insulation | EPD | UL | USA | Northamerica | 2014 | 2019 | 1 kg of insulation material plus 1 m2 ASJ+ with a building service life of 60 years | TRACI 2.0 |  |  | 5.89
Insulation - hydronic water Insulation | FIBERGLAS™ PIPE INSULATION | insulation | NO WRAP | Owens Corning | EPD | UL | USA | Northamerica | 2015 | 2020 | 1 kg of insulation material plus 1 m2 jacket with a building service life of 60 years |  |  |  | 6.52
| SUSTAINABLE INSULATION ® | insulation | FSK Faced -Fiberglass Duct Wrap Insulation | CertainTeed Corporation | EPD | UL | USA | Northamerica | 02.02.2017 | 02.02.2021 | 1 kilogram of insulation material plus 1 square meter of facing with a building service life of 60 years. | TRACI 2.0 |  |  | 2.56
Note on A2: Monica: This name is used in the VLOOKUP formula. Empty cells are LCA data sources not used in the study. These other sources were left here to indicate when more than one source was found.

## Custom quantities input
Category | Building type | Building size range [sf] | Building base size [sf] | Building Size Category | Building model | System type | Subsystem description | Item type | Item name | Midpoint of material quantity estimate (calculated) [kg/m2] | Cooling load (capacity of equipment), min [sf/ton] | Cooling load (capacity of equipment), max [sf/ton] | Heating load (capacity of equipment), min [BTUH/sf] | Heating load (capacity of equipment), max [BTUH/sf] | GWP [kg CO2e/m2]
Mechanical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Packaged rooftop heat pump | NA | Material | Galv sheet metal | 6.443 | 350 | 500 | 12 | 18 | 15.4632
Mechanical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Packaged rooftop heat pump | NA | Material | Flexible duct | 0.17937 | 350 | 500 | 12 | 18 | 0.95606
Mechanical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Packaged rooftop heat pump | NA | Material | Insulation - duct wrap | 0.34097 | 350 | 500 | 12 | 18 | 1.9401
Mechanical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Packaged rooftop heat pump | NA | Material | Insulation - hydronic water insulation | 0.19484 | 350 | 500 | 12 | 18 | 1.2703
Mechanical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Packaged rooftop heat pump | NA | Material | Refrigerants | 0.019484 | 350 | 500 | 12 | 18 | 36.8245
Mechanical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Packaged rooftop AC + Furnace | NA | Material | Galv sheet metal | 8.9128 | 350 | 500 | 12 | 18 | 21.3907
Mechanical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Packaged rooftop AC + Furnace | NA | Material | Flexible duct | 0.17937 | 350 | 500 | 12 | 18 | 0.95606
Mechanical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Packaged rooftop AC + Furnace | NA | Material | Insulation - duct wrap | 0.34097 | 350 | 500 | 12 | 18 | 1.9401
Mechanical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Packaged rooftop AC + Furnace | NA | Material | Insulation - hydronic water insulation | 0.19484 | 350 | 500 | 12 | 18 | 1.2703
Mechanical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Packaged rooftop AC + Furnace | NA | Material | Refrigerants | 0.019484 | 350 | 500 | 12 | 18 | 36.8245
Mechanical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Packaged rooftop heat pump | NA | Equipment | Packaged units | 3.1339 | 350 | 500 | 12 | 18 | 9.8465
Mechanical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Packaged rooftop AC + Furnace | NA | Equipment | Packaged units | 3.1339 | 350 | 500 | 12 | 18 | 9.8465
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | DOAS ERV + VRF | NA | Material | Galv sheet metal | 4.871 | 400 | 600 | 10 | 15 | 11.6903
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | DOAS ERV + VRF | NA | Material | Flexible duct | 0.19399 | 400 | 600 | 10 | 15 | 1.0339
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | DOAS ERV + VRF | NA | Material | Copper pipe | 1.3191 | 400 | 600 | 10 | 15 | 2.8887
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | DOAS ERV + VRF | NA | Material | Insulation - duct wrap | 0.34097 | 400 | 600 | 10 | 15 | 1.9401
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | DOAS ERV + VRF | NA | Material | Insulation - hydronic water insulation | 0.19484 | 400 | 600 | 10 | 15 | 1.2703
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | DOAS ERV + VRF | NA | Material | Refrigerants | 0.019484 | 400 | 600 | 10 | 15 | 36.8245
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Material | Galv sheet metal | 7.6158 | 400 | 600 | 10 | 15 | 18.2778
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Material | Flexible duct | 1.7722 | 400 | 600 | 10 | 15 | 9.4457
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Material | Insulation - duct wrap | 0.34097 | 400 | 600 | 10 | 15 | 1.9401
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Material | Insulation - hydronic water insulation | 0.19484 | 400 | 600 | 10 | 15 | 1.2703
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Material | Refrigerants | 0.019484 | 400 | 600 | 10 | 15 | 36.8245
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | DOAS ERV + VRF | NA | Equipment | DOAS ERV w/ electric heat | 2.0458 | 400 | 600 | 10 | 15 | 10.201
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | DOAS ERV + VRF | NA | Equipment | VRF outdoor units | 2.8556 | 400 | 600 | 10 | 15 | 10.9316
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | DOAS ERV + VRF | NA | Equipment | VRF casettes | 1.3249 | 400 | 600 | 10 | 15 | 5.4414
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Equipment | DOAS ERV w/ electric heat | 1.9484 | 400 | 600 | 10 | 15 | 9.7153
Mechanical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Equipment | Packaged units | 1.8315 | 400 | 600 | 10 | 15 | 5.7544
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Basic LTG & Power | Cable | Material | Non-Metallic Cable | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Basic LTG & Power | Utility transformer pole mounted or outside property | Equipment | Transformer | 0.29226 | NA | NA | NA | NA | 0.15142
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Basic LTG & Power | Battery backup for emergency egress lighting and life safety sytems | Equipment | Battery 20W unit | 0.34793 | NA | NA | NA | NA | 4.0541
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Basic LTG & Power | Code minimum time clock controlled lighting system. (Nothing "Auto") | Material | Non-Metallic Cable | 0.24708 | NA | NA | NA | NA | 0.072519
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Basic LTG & Power | Fluorescent Lighting | Equipment | Fixtures | 0.54555 | NA | NA | NA | NA | 0.1922
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Basic LTG & Power | Fluorescent Lighting | Material | Non-metallic boxes | 0.028112 | NA | NA | NA | NA | 0.089679
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Basic LTG & Power | Aluminum feeder wire 100amps and over | Equipment | Feeder Wire | 0.14126 | NA | NA | NA | NA | 0.012192
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Basic LTG & Power | Retail meter center or 6 disconnect basic service switchgear | Equipment | Basic Service Switchgear | 0.021777 | NA | NA | NA | NA | 0.011283
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Basic LTG & Power | Cable | Material | D-Rings 0.15 lbs/EA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Basic LTG & Power | Cable | Material | Non-Metallic Cable | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Basic LTG & Power | Utility transformer pole mounted or outside property | Equipment | Transformer | 0.29226 | NA | NA | NA | NA | 0.15142
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Basic LTG & Power | Battery backup for emergency egress lighting and life safety sytems | Equipment | Battery 20W unit | 0.34793 | NA | NA | NA | NA | 4.0541
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Basic LTG & Power | Code minimum time clock controlled lighting system. (Nothing "Auto") | Material | Non-Metallic Cable | 0.24708 | NA | NA | NA | NA | 0.072519
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Basic LTG & Power | Fluorescent Lighting | Equipment | Fixtures | 0.54555 | NA | NA | NA | NA | 0.1922
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Basic LTG & Power | Fluorescent Lighting | Material | Non-metallic boxes | 0.028112 | NA | NA | NA | NA | 0.089679
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Basic LTG & Power | Aluminum feeder wire 100amps and over | Equipment | Feeder Wire | 0.14126 | NA | NA | NA | NA | 0.012192
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Basic LTG & Power | Retail meter center or 6 disconnect basic service switchgear | Equipment | Basic Service Switchgear | 0.021777 | NA | NA | NA | NA | 0.011283
Electrical | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Basic LTG & Power | Cable | Material | D-Rings 0.15 lbs/EA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | Commercial LTG/PWR | Utility transformer pole mounted or outside property | Material | MC Cable (metallic cable) | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | Commercial LTG/PWR | Utility transformer pole mounted or outside property | Equipment | Transformer | 2.9226 | NA | NA | NA | NA | 1.5142
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | Commercial LTG/PWR | battery backup for emergency egress lighting and life safety sytems | Equipment | Battery 20W unit | 0.34793 | NA | NA | NA | NA | 4.0541
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming) | Equipment | Occupancy sensors | 0.0012379 | NA | NA | NA | NA | 0.0055706
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming) | Material | MC Cable (metallic cable) | 0.33693 | NA | NA | NA | NA | 0.029081
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | Commercial LTG/PWR | LED Lighting | Equipment | LED fixtures | 0.58452 | NA | NA | NA | NA | 6.605
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | Commercial LTG/PWR | LED Lighting | Equipment | Metal boxes | 0.050101 | NA | NA | NA | NA | 0.0043243
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | Commercial LTG/PWR | Copper feeder wire | Equipment | Feeder wire | 0.78969 | NA | NA | NA | NA | 0.068158
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | Commercial LTG/PWR | Copper feeder wire | Equipment | EMT conduit | 0.37764 | NA | NA | NA | NA | 1.0649
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | Commercial LTG/PWR | Utility transformer pole mounted or outside property | Material | MC Cable (metallic cable) | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | Commercial LTG/PWR | Utility transformer pole mounted or outside property | Equipment | Transformer | 2.9226 | NA | NA | NA | NA | 1.5142
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | Commercial LTG/PWR | battery backup for emergency egress lighting and life safety sytems | Equipment | Battery 20W unit | 0.34793 | NA | NA | NA | NA | 4.0541
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming) | Equipment | Occupancy sensors | 0.0012379 | NA | NA | NA | NA | 0.0055706
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming) | Material | MC Cable (metallic cable) | 0.33693 | NA | NA | NA | NA | 0.029081
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | Commercial LTG/PWR | LED Lighting | Equipment | LED fixtures | 0.58452 | NA | NA | NA | NA | 6.605
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | Commercial LTG/PWR | LED Lighting | Equipment | Metal boxes | 0.050101 | NA | NA | NA | NA | 0.0043243
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | Commercial LTG/PWR | Copper feeder wire | Equipment | Feeder wire | 0.78969 | NA | NA | NA | NA | 0.068158
Electrical | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | Commercial LTG/PWR | Copper feeder wire | Equipment | EMT conduit | 0.37764 | NA | NA | NA | NA | 1.0649
Plumbing | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Water | NA | Material | Copper pipe | 0.83655 | NA | NA | NA | NA | 1.832
Plumbing | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Water | NA | Material | PEX water pipe | 0.089133 | NA | NA | NA | NA | 0.42873
Plumbing | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Waste & Vent | NA | Material | Cast iron pipe | 1.5459 | NA | NA | NA | NA | 4.4521
Plumbing | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard a | Waste & Vent | NA | Material | PVC | 0.15379 | NA | NA | NA | NA | 0.49061
Plumbing | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Water | NA | Material | Copper pipe | 0.83655 | NA | NA | NA | NA | 1.832
Plumbing | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Water | NA | Material | PEX water pipe | 0.089133 | NA | NA | NA | NA | 0.42873
Plumbing | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Waste & Vent | NA | Material | Cast iron pipe | 1.5459 | NA | NA | NA | NA | 4.4521
Plumbing | Standard | 2000-25000 | 7000 | XSmall | XSmall Standard b | Waste & Vent | NA | Material | PVC | 0.15379 | NA | NA | NA | NA | 0.49061
Plumbing | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | Water | NA | Material | Copper pipe | 0.83655 | NA | NA | NA | NA | 1.832
Plumbing | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | Water | NA | Material | PEX water pipe | 0.089133 | NA | NA | NA | NA | 0.42873
Plumbing | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | Waste & Vent | NA | Material | Cast iron pipe | 1.5459 | NA | NA | NA | NA | 4.4521
Plumbing | High performance | 2000-25000 | 7000 | XSmall | XSmall HP a | Waste & Vent | NA | Material | PVC | 0.15379 | NA | NA | NA | NA | 0.49061
Plumbing | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | Water | NA | Material | Copper pipe | 0.83655 | NA | NA | NA | NA | 1.832
Plumbing | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | Water | NA | Material | PEX water pipe | 0.089133 | NA | NA | NA | NA | 0.42873
Plumbing | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | Waste & Vent | NA | Material | Cast iron pipe | 1.5459 | NA | NA | NA | NA | 4.4521
Plumbing | High performance | 2000-25000 | 7000 | XSmall | XSmall HP b | Waste & Vent | NA | Material | PVC | 0.15379 | NA | NA | NA | NA | 0.49061
Mechanical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Packaged rooftop heat pump | NA | Equipment | Packaged units | 2.6017 | 350 | 500 | 12 | 18 | 8.1744
Mechanical | Standard | 10000-80000 | 25000 | Small | Small Standard b | VAV AHU w/ PFP Terminals | NA | Equipment | VAV AHU w/ DX | 2.7844 | 350 | 500 | 12 | 18 | 18.9134
Mechanical | Standard | 10000-80000 | 25000 | Small | Small Standard b | VAV AHU w/ PFP Terminals | NA | Equipment | VAV Terminals w/ electric heat | 1.0899 | 350 | 500 | 12 | 18 | 4.4762
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP a | DOAS ERV + VRF | NA | Material | Galv sheet metal | 5.6698 | 400 | 600 | 10 | 15 | 13.6075
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP a | DOAS ERV + VRF | NA | Material | Flexible duct | 0.18778 | 400 | 600 | 10 | 15 | 1.0008
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP a | DOAS ERV + VRF | NA | Material | Copper pipe | 1.2014 | 400 | 600 | 10 | 15 | 2.6311
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP a | DOAS ERV + VRF | NA | Material | Insulation - duct wrap | 0.34097 | 400 | 600 | 10 | 15 | 1.9401
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP a | DOAS ERV + VRF | NA | Material | Insulation - hydronic water insulation | 0.19484 | 400 | 600 | 10 | 15 | 1.2703
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP a | DOAS ERV + VRF | NA | Material | Refrigerants | 0.019484 | 400 | 600 | 10 | 15 | 36.8245
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Material | Galv sheet metal | 7.0276 | 400 | 600 | 10 | 15 | 16.8662
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Material | Flexible duct | 0.18591 | 400 | 600 | 10 | 15 | 0.99091
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Material | Insulation - duct wrap | 0.34097 | 400 | 600 | 10 | 15 | 1.9401
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Material | Insulation - hydronic water insulation | 0.19484 | 400 | 600 | 10 | 15 | 1.2703
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Material | Refrigerants | 0.019484 | 400 | 600 | 10 | 15 | 36.8245
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP a | DOAS ERV + VRF | NA | Equipment | DOAS ERV w/ electric heat | 2.0458 | 400 | 600 | 10 | 15 | 10.201
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP a | DOAS ERV + VRF | NA | Equipment | VRF outdoor units | 1.9734 | 400 | 600 | 10 | 15 | 7.5542
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP a | DOAS ERV + VRF | NA | Equipment | VRF casettes | 0.9401 | 400 | 600 | 10 | 15 | 3.861
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Equipment | DOAS ERV w/ electric heat | 1.773 | 400 | 600 | 10 | 15 | 8.8409
Mechanical | High performance | 10000-80000 | 25000 | Small | Small HP b | DOAS ERV + Packaged Rooftop Heat Pump | NA | Equipment | Packaged units | 1.8899 | 400 | 600 | 10 | 15 | 5.9381
Mechanical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Packaged rooftop heat pump | NA | Material | Galv sheet metal | 6.443 | 350 | 500 | 12 | 18 | 15.4632
Mechanical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Packaged rooftop heat pump | NA | Material | Flexible duct | 0.17523 | 350 | 500 | 12 | 18 | 0.93399
Mechanical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Packaged rooftop heat pump | NA | Material | Insulation - duct wrap | 0.34097 | 350 | 500 | 12 | 18 | 1.9401
Mechanical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Packaged rooftop heat pump | NA | Material | Insulation - hydronic water insulation | 0.19484 | 350 | 500 | 12 | 18 | 1.2703
Mechanical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Packaged rooftop heat pump | NA | Material | Refrigerants | 0.019484 | 350 | 500 | 12 | 18 | 36.8245
Mechanical | Standard | 10000-80000 | 25000 | Small | Small Standard b | VAV AHU w/ PFP Terminals | NA | Material | Galv sheet metal | 6.8548 | 350 | 500 | 12 | 18 | 16.4516
Mechanical | Standard | 10000-80000 | 25000 | Small | Small Standard b | VAV AHU w/ PFP Terminals | NA | Material | Flexible duct | 0.17306 | 350 | 500 | 12 | 18 | 0.92241
Mechanical | Standard | 10000-80000 | 25000 | Small | Small Standard b | VAV AHU w/ PFP Terminals | NA | Material | Insulation - duct wrap | 0.34097 | 350 | 500 | 12 | 18 | 1.9401
Mechanical | Standard | 10000-80000 | 25000 | Small | Small Standard b | VAV AHU w/ PFP Terminals | NA | Material | Insulation - hydronic water insulation | 0.19484 | 350 | 500 | 12 | 18 | 1.2703
Mechanical | Standard | 10000-80000 | 25000 | Small | Small Standard b | VAV AHU w/ PFP Terminals | NA | Material | Refrigerants | 0.019484 | 350 | 500 | 12 | 18 | 36.8245
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Commercial LTG/PWR | Utility transformer pole mounted or outside property pad mounted | Equipment | Transformer | 3.8578 | NA | NA | NA | NA | 1.9987
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Commercial LTG/PWR | Battery backup for emergency egress lighting and life safety sytems | Equipment | Battery 20W unit | 0.34798 | NA | NA | NA | NA | 4.0547
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Commercial LTG/PWR | code minimum time clock controlled lighting system ( Occupancy Sensors in offices) | Material | MC Cable (metallic cable) | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Commercial LTG/PWR | Fluorescent Lighting | Equipment | Fixtures | 0.54555 | NA | NA | NA | NA | 0.1922
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Commercial LTG/PWR | Fluorescent Lighting | Material | Metal boxes | 0.049879 | NA | NA | NA | NA | 0.004305
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Commercial LTG/PWR | 800A 480v Distribution | Material | Aluminum feeders 100amp and over | 0.46493 | NA | NA | NA | NA | 0.040128
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Commercial LTG/PWR | 800A 480v Distribution | Material | MC Cable (metallic cable) | 0.43839 | NA | NA | NA | NA | 0.037837
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Commercial LTG/PWR | NA | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Commercial LTG/PWR | Data/WAP (Wireless) | Equipment | Data/WAP (Wireless) | 0.03585 | NA | NA | NA | NA | 0.0030942
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Commercial LTG/PWR | Data/WAP (Wireless) | Material | D-Rings 0.15 lbs/EA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard a | Commercial LTG/PWR | FA | Equipment | FA | 0.015982 | NA | NA | NA | NA | 0.0013794
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard b | Commercial LTG/PWR | Utility transformer pole mounted or outside property pad mounted | Equipment | Transformer | 3.8578 | NA | NA | NA | NA | 1.9987
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard b | Commercial LTG/PWR | Battery backup for emergency egress lighting and life safety sytems | Equipment | Battery 20W unit | 0.34798 | NA | NA | NA | NA | 4.0547
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard b | Commercial LTG/PWR | code minimum time clock controlled lighting system ( Occupancy Sensors in offices) | Material | MC Cable (metallic cable) | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard b | Commercial LTG/PWR | Fluorescent Lighting | Equipment | Fixtures | 0.54555 | NA | NA | NA | NA | 0.1922
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard b | Commercial LTG/PWR | Fluorescent Lighting | Material | Metal boxes | 0.049879 | NA | NA | NA | NA | 0.004305
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard b | Commercial LTG/PWR | 800A 480v Distribution | Material | Aluminum feeders 100amp and over | 0.46493 | NA | NA | NA | NA | 0.040128
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard b | Commercial LTG/PWR | 800A 480v Distribution | Material | MC Cable (metallic cable) | 0.43839 | NA | NA | NA | NA | 0.037837
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard b | Commercial LTG/PWR | NA | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard b | Commercial LTG/PWR | Data/WAP (Wireless) | Equipment | Data/WAP (Wireless) | 0.03585 | NA | NA | NA | NA | 0.0030942
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard b | Commercial LTG/PWR | Data/WAP (Wireless) | Material | D-Rings 0.15 lbs/EA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 10000-80000 | 25000 | Small | Small Standard b | Commercial LTG/PWR | FA | Equipment | FA | 0.015982 | NA | NA | NA | NA | 0.0013794
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP a | Commercial LTG/PWR | Energy meters for branch circuit monitoring by system | Equipment | Energy meters, 0.59 lbs/EA | 0.0031856 | NA | NA | NA | NA | 0.041413
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP a | Commercial LTG/PWR | Data + other LV | Material | EMT conduit | 0.027414 | NA | NA | NA | NA | 0.077307
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP a | Commercial LTG/PWR | Utility transformer pole mounted or outside property pad mounted | Equipment | Transformer | 2.5076 | NA | NA | NA | NA | 1.2992
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP a | Commercial LTG/PWR | Backup generator for life safety systems 350kw diesel | Equipment | Battery | 0.19513 | NA | NA | NA | NA | 2.2736
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP a | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming) | Equipment | Occupancy sensors | 0.0013917 | NA | NA | NA | NA | 0.0062627
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP a | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming) | Material | EMT conduit | 1.4235 | NA | NA | NA | NA | 4.0143
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP a | Commercial LTG/PWR | LED Lighting | Equipment | LED fixtures | 0.58452 | NA | NA | NA | NA | 6.605
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP a | Commercial LTG/PWR | LED Lighting | Material | Metal boxes | 0.049829 | NA | NA | NA | NA | 0.0043008
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP a | Commercial LTG/PWR | Daylight Sensors | Equipment | Daylight sensors | 0.00073065 | NA | NA | NA | NA | 0.0032879
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP a | Commercial LTG/PWR | 800A 480v Distribution | Material | Copper feeders | 0.7646 | NA | NA | NA | NA | 0.065993
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP a | Commercial LTG/PWR | 800A 480v Distribution | Material | EMT conduit | 0.54622 | NA | NA | NA | NA | 1.5403
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP a | Commercial LTG/PWR | Energy meters for branch circuit monitoring by system |  |  | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP b | Commercial LTG/PWR | Energy meters for branch circuit monitoring by system | Equipment | Energy meters, 0.59 lbs/EA | 0.0031856 | NA | NA | NA | NA | 0.041413
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP b | Commercial LTG/PWR | Data + other LV | Material | EMT conduit | 0.027414 | NA | NA | NA | NA | 0.077307
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP b | Commercial LTG/PWR | Utility transformer pole mounted or outside property pad mounted | Equipment | Transformer | 2.5076 | NA | NA | NA | NA | 1.2992
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP b | Commercial LTG/PWR | Backup generator for life safety systems 350kw diesel | Equipment | Battery | 0.19513 | NA | NA | NA | NA | 2.2736
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP b | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming) | Equipment | Occupancy sensors | 0.0013917 | NA | NA | NA | NA | 0.0062627
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP b | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming) | Material | EMT conduit | 1.4235 | NA | NA | NA | NA | 4.0143
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP b | Commercial LTG/PWR | LED Lighting | Equipment | LED fixtures | 0.58452 | NA | NA | NA | NA | 6.605
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP b | Commercial LTG/PWR | LED Lighting | Material | Metal boxes | 0.049829 | NA | NA | NA | NA | 0.0043008
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP b | Commercial LTG/PWR | Daylight Sensors | Equipment | Daylight sensors | 0.00073065 | NA | NA | NA | NA | 0.0032879
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP b | Commercial LTG/PWR | 800A 480v Distribution | Material | Copper feeders | 0.7646 | NA | NA | NA | NA | 0.065993
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP b | Commercial LTG/PWR | 800A 480v Distribution | Material | EMT conduit | 0.54622 | NA | NA | NA | NA | 1.5403
Electrical | High performance | 10000-80000 | 25000 | Small | Small HP b | Commercial LTG/PWR | Energy meters for branch circuit monitoring by system |  |  | 0 | NA | NA | NA | NA | 0
Plumbing | Standard | 10000-80000 | 25000 | Small | Small Standard a | Water | NA | Material | Copper pipe | 0.97853 | NA | NA | NA | NA | 2.143
Plumbing | Standard | 10000-80000 | 25000 | Small | Small Standard a | Waste & Vent | NA | Material | Cast iron pipe | 1.5438 | NA | NA | NA | NA | 4.4461
Plumbing | Standard | 10000-80000 | 25000 | Small | Small Standard a | Waste & Vent | NA | Material | PVC | 0.15379 | NA | NA | NA | NA | 0.49061
Plumbing | Standard | 10000-80000 | 25000 | Small | Small Standard b | Water | NA | Material | Copper pipe | 0.97853 | NA | NA | NA | NA | 2.143
Plumbing | Standard | 10000-80000 | 25000 | Small | Small Standard b | Waste & Vent | NA | Material | Cast iron pipe | 1.5438 | NA | NA | NA | NA | 4.4461
Plumbing | Standard | 10000-80000 | 25000 | Small | Small Standard b | Waste & Vent | NA | Material | PVC | 0.15379 | NA | NA | NA | NA | 0.49061
Plumbing | High performance | 10000-80000 | 25000 | Small | Small HP a | Water | NA | Material | Copper pipe | 0.97853 | NA | NA | NA | NA | 2.143
Plumbing | High performance | 10000-80000 | 25000 | Small | Small HP a | Waste & Vent | NA | Material | Cast iron pipe | 1.5438 | NA | NA | NA | NA | 4.4461
Plumbing | High performance | 10000-80000 | 25000 | Small | Small HP a | Waste & Vent | NA | Material | PVC | 0.15379 | NA | NA | NA | NA | 0.49061
Plumbing | High performance | 10000-80000 | 25000 | Small | Small HP b | Water | NA | Material | Copper pipe | 0.97853 | NA | NA | NA | NA | 2.143
Plumbing | High performance | 10000-80000 | 25000 | Small | Small HP b | Waste & Vent | NA | Material | Cast iron pipe | 1.5438 | NA | NA | NA | NA | 4.4461
Plumbing | High performance | 10000-80000 | 25000 | Small | Small HP b | Waste & Vent | NA | Material | PVC | 0.15379 | NA | NA | NA | NA | 0.49061
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | VAV AHU w/ PFP Terminals | NA | Equipment | VAV AHU w/ DX | 3.6843 | 350 | 500 | 12 | 18 | 25.0263
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | VAV AHU w/ PFP Terminals | NA | Equipment | VAV Terminals w/ electric heat | 0.70142 | 350 | 500 | 12 | 18 | 2.8807
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | WSHP | NA | Equipment | Cooling tower | 2.0971 | 350 | 500 | 12 | 18 | 10.4568
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | WSHP | NA | Equipment | Boiler | 0.42164 | 350 | 500 | 12 | 18 | 5.1238
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | WSHP | NA | Equipment | Distributed zone WSHP | 2.2212 | 350 | 500 | 12 | 18 | 4.2464
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | WSHP | NA | Equipment | Pumps | 0.59487 | 350 | 500 | 12 | 18 | 1.1373
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | DOAS + VRF | NA | Material | Galv sheet metal | 4.793 | 400 | 600 | 10 | 15 | 11.5033
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | DOAS + VRF | NA | Material | Flexible duct | 0.18364 | 400 | 600 | 10 | 15 | 0.97878
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | DOAS + VRF | NA | Material | Copper pipe | 0.89334 | 400 | 600 | 10 | 15 | 1.9564
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | DOAS + VRF | NA | Material | Insulation - duct wrap | 0.34097 | 400 | 600 | 10 | 15 | 1.9401
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | DOAS + VRF | NA | Material | Insulation - hydronic water insulation | 0.19484 | 400 | 600 | 10 | 15 | 1.2703
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | DOAS + VRF | NA | Material | Refrigerants | 0.019484 | 400 | 600 | 10 | 15 | 36.8245
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | DOAS + WSHP | NA | Material | Galv sheet metal | 6.929 | 400 | 600 | 10 | 15 | 16.6296
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | DOAS + WSHP | NA | Material | Flexible duct | 0.18364 | 400 | 600 | 10 | 15 | 0.97878
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | DOAS + WSHP | NA | Material | Steel pipe | 1.1848 | 400 | 600 | 10 | 15 | 2.6729
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | DOAS + WSHP | NA | Material | Copper pipe | 0.82884 | 400 | 600 | 10 | 15 | 1.8152
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | DOAS + WSHP | NA | Material | Insulation - duct wrap | 0.34097 | 400 | 600 | 10 | 15 | 1.9401
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | DOAS + WSHP | NA | Material | Insulation - hydronic water insulation | 0.19484 | 400 | 600 | 10 | 15 | 1.2703
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | DOAS + WSHP | NA | Material | Refrigerants | 0.019484 | 400 | 600 | 10 | 15 | 36.8245
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | DOAS + VRF | NA | Equipment | DOAS w/ heat recovery | 2.2406 | 400 | 600 | 10 | 15 | 8.5775
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | DOAS + VRF | NA | Equipment | Single duct VAVs or CAVs | 0.86703 | 400 | 600 | 10 | 15 | 3.5609
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | DOAS + VRF | NA | Equipment | VRF outdoor units | 1.3639 | 400 | 600 | 10 | 15 | 5.2211
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | DOAS + VRF | NA | Equipment | VRF fan coils | 1.1788 | 400 | 600 | 10 | 15 | 4.8413
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | DOAS + WSHP | NA | Equipment | DOAS w/ heat recovery | 2.2406 | 400 | 600 | 10 | 15 | 8.5775
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | DOAS + WSHP | NA | Equipment | Single duct VAVs or CAVs | 0.86703 | 400 | 600 | 10 | 15 | 3.5609
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | DOAS + WSHP | NA | Equipment | Cooling tower | 1.9217 | 400 | 600 | 10 | 15 | 9.5824
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | DOAS + WSHP | NA | Equipment | Boiler | 0.65545 | 400 | 600 | 10 | 15 | 7.965
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | DOAS + WSHP | NA | Equipment | Distributed zone WSHP | 1.5782 | 400 | 600 | 10 | 15 | 3.0172
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | VAV AHU w/ PFP Terminals | NA | Material | Galv sheet metal | 6.7439 | 350 | 500 | 12 | 18 | 16.1853
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | VAV AHU w/ PFP Terminals | NA | Material | Flexible duct | 0.17316 | 350 | 500 | 12 | 18 | 0.92296
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | VAV AHU w/ PFP Terminals | NA | Material | Insulation - duct wrap | 0.34097 | 350 | 500 | 12 | 18 | 1.9401
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | VAV AHU w/ PFP Terminals | NA | Material | Insulation - hydronic water insulation | 0.19484 | 350 | 500 | 12 | 18 | 1.2703
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | VAV AHU w/ PFP Terminals | NA | Material | Refrigerants | 0.019484 | 350 | 500 | 12 | 18 | 36.8245
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | WSHP | NA | Material | Galv sheet metal | 5.6601 | 350 | 500 | 12 | 18 | 13.5842
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | WSHP | NA | Material | Flexible duct | 0.17316 | 350 | 500 | 12 | 18 | 0.92296
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | WSHP | NA | Material | Steel pipe | 1.1868 | 350 | 500 | 12 | 18 | 2.6774
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | WSHP | NA | Material | Copper pipe | 0.85938 | 350 | 500 | 12 | 18 | 1.8821
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | WSHP | NA | Material | Insulation - duct wrap | 0.34097 | 350 | 500 | 12 | 18 | 1.9401
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | WSHP | NA | Material | Insulation - hydronic water insulation | 0.19484 | 350 | 500 | 12 | 18 | 1.2703
Mechanical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | WSHP | NA | Material | Refrigerants | 0.019484 | 350 | 500 | 12 | 18 | 36.8245
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Commercial LTG/PWR | In building utility transformer vault and oil filled transformers | Equipment | Transformer vault | 0.53445 | NA | NA | NA | NA | 0.2769
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Commercial LTG/PWR | battery backup for emergency egress lighting and life safety sytems | Equipment | Battery 20W unit | 0.34793 | NA | NA | NA | NA | 4.0541
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Commercial LTG/PWR | code minimum time clock controlled lighting system ( Occupancy Sensors in offices) | Equipment | Code minimum time clock, 0.68 lbs/EA | 0.0014004 | NA | NA | NA | NA | 0.00012087
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Commercial LTG/PWR | LED Lighting | Equipment | LED fixtures | 0.58452 | NA | NA | NA | NA | 6.605
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Commercial LTG/PWR | Daylight Sensors | Equipment | Daylight sensors | 0.00073065 | NA | NA | NA | NA | 0.0032879
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Commercial LTG/PWR | 1200A Distribution | Material | Aluminum feeders 100amp and over | 0.18899 | NA | NA | NA | NA | 0.016312
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Commercial LTG/PWR | 1200A Distribution | Material | MC Cable (metallic cable) | 0.67841 | NA | NA | NA | NA | 0.058554
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Commercial LTG/PWR |  |  | NA | 0.052487 | NA | NA | NA | NA | 0
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Commercial LTG/PWR | DATA/AV/Access CNTRL | Equipment | DATA/AV/Access CNTRL | 0.11034 | NA | NA | NA | NA | 0.69738
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Commercial LTG/PWR | DATA/AV/Access CNTRL | Material | D-Rings 0.15 lbs/EA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Commercial LTG/PWR | FA | Equipment | FA | 0.030824 | NA | NA | NA | NA | 0.0026605
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Commercial LTG/PWR | In building utility transformer vault and oil filled transformers | Equipment | Transformer vault | 0.53445 | NA | NA | NA | NA | 0.2769
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Commercial LTG/PWR | battery backup for emergency egress lighting and life safety sytems | Equipment | Battery 20W unit | 0.34793 | NA | NA | NA | NA | 4.0541
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Commercial LTG/PWR | code minimum time clock controlled lighting system ( Occupancy Sensors in offices) | Equipment | Code minimum time clock, 0.68 lbs/EA | 0.0014004 | NA | NA | NA | NA | 0.00012087
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Commercial LTG/PWR | LED Lighting | Equipment | LED fixtures | 0.58452 | NA | NA | NA | NA | 6.605
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Commercial LTG/PWR | Daylight Sensors | Equipment | Daylight sensors | 0.00073065 | NA | NA | NA | NA | 0.0032879
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Commercial LTG/PWR | 1200A Distribution | Material | Aluminum feeders 100amp and over | 0.18899 | NA | NA | NA | NA | 0.016312
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Commercial LTG/PWR | 1200A Distribution | Material | MC Cable (metallic cable) | 0.67841 | NA | NA | NA | NA | 0.058554
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Commercial LTG/PWR |  |  | NA | 0.052487 | NA | NA | NA | NA | 0
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Commercial LTG/PWR | DATA/AV/Access CNTRL | Equipment | DATA/AV/Access CNTRL | 0.11034 | NA | NA | NA | NA | 0.69738
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Commercial LTG/PWR | DATA/AV/Access CNTRL | Material | D-Rings 0.15 lbs/EA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Commercial LTG/PWR | FA | Equipment | FA | 0.030824 | NA | NA | NA | NA | 0.0026605
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | DATA/AV/Access CNTRL | Equipment | DATA/AV/Access CNTRL | 0.011177 | NA | NA | NA | NA | 0.070639
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | DATA/AV/Access CNTRL | Material | EMT conduit | 0.0097846 | NA | NA | NA | NA | 0.027593
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | FA | Equipment | FA | 0.0050232 | NA | NA | NA | NA | 0.00043355
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | In building utility transformer vault and oil filled transformers | Equipment | Transformer vault | 0.49894 | NA | NA | NA | NA | 0.2585
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | In building utility transformer vault and oil filled transformers | Equipment | Transformer vault | 0.49894 | NA | NA | NA | NA | 0.2585
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | Backup generator for life safety systems 500kw diesel | Equipment | Backup Generator | 0.57042 | NA | NA | NA | NA | 0.29553
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | Backup generator for life safety systems 500kw diesel | Equipment | Backup Generator | 0.57042 | NA | NA | NA | NA | 0.29553
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming, addressable fixtures) | Equipment | Occupancy sensors | 0.0015043 | NA | NA | NA | NA | 0.0067692
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming, addressable fixtures) | Equipment | Occupancy sensors | 0.0015043 | NA | NA | NA | NA | 0.0067692
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | LED Lighting | Equipment | LED fixtures | 0.58452 | NA | NA | NA | NA | 6.605
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | LED Lighting | Equipment | LED fixtures | 0.58452 | NA | NA | NA | NA | 6.605
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | Daylight Sensors,Addressable LTG | Equipment | Daylight sensors | 0.0008305 | NA | NA | NA | NA | 0.0037373
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | Daylight Sensors,Addressable LTG | Equipment | Daylight sensors | 0.0008305 | NA | NA | NA | NA | 0.0037373
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | 2500A Distribution | Material | Copper feeders | 0.31306 | NA | NA | NA | NA | 0.027021
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | 2500A Distribution | Material | Copper feeders | 0.31306 | NA | NA | NA | NA | 0.027021
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | Energy meters for branch circuit monitoring by system | Material | EMT conduit | 0.54622 | NA | NA | NA | NA | 1.5403
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | Energy meters for branch circuit monitoring by system | Material | EMT conduit | 0.54622 | NA | NA | NA | NA | 1.5403
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | VFD | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | VFD | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | PV (2000w Solar) | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | PV (2000w Solar) | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | Energy meters for branch circuit monitoring by system | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | Energy meters for branch circuit monitoring by system | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | DATA/AV/Access CNTRL | Material | EMT conduit | 0.0030577 | NA | NA | NA | NA | 0.0086227
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | DATA/AV/Access CNTRL | Equipment | DATA/AV/Access CNTRL | 0.035741 | NA | NA | NA | NA | 0.22588
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Commercial LTG/PWR | DAS - Cellular and emergency radio | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | DAS - Cellular and emergency radio | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Commercial LTG/PWR | FA | Equipment | FA | 0.016074 | NA | NA | NA | NA | 0.0013874
Plumbing | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Water | NA | Material | Copper pipe | 0.81377 | NA | NA | NA | NA | 1.7822
Plumbing | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Water | NA | Material | Stainless steel | 0.077061 | NA | NA | NA | NA | 0.17385
Plumbing | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Waste & Vent | NA | Material | Cast iron pipe | 1.3832 | NA | NA | NA | NA | 3.9835
Plumbing | Standard | 20000-300000 | 80000 | Medium | Medium Standard a | Waste & Vent | NA | Material | PVC | 0.13504 | NA | NA | NA | NA | 0.43078
Plumbing | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Water | NA | Material | Copper pipe | 0.81377 | NA | NA | NA | NA | 1.7822
Plumbing | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Water | NA | Material | Stainless steel | 0.077061 | NA | NA | NA | NA | 0.17385
Plumbing | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Waste & Vent | NA | Material | Cast iron pipe | 1.3832 | NA | NA | NA | NA | 3.9835
Plumbing | Standard | 20000-300000 | 80000 | Medium | Medium Standard b | Waste & Vent | NA | Material | PVC | 0.13504 | NA | NA | NA | NA | 0.43078
Plumbing | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Water | NA | Material | Copper pipe | 0.81377 | NA | NA | NA | NA | 1.7822
Plumbing | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Water | NA | Material | Stainless steel | 0.077061 | NA | NA | NA | NA | 0.17385
Plumbing | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Waste & Vent | NA | Material | Cast iron pipe | 1.3832 | NA | NA | NA | NA | 3.9835
Plumbing | High performance | 20000-300000 | 80000 | Medium | Medium HP a | Waste & Vent | NA | Material | PVC | 0.13504 | NA | NA | NA | NA | 0.43078
Plumbing | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Water | NA | Material | Copper pipe | 0.81377 | NA | NA | NA | NA | 1.7822
Plumbing | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Water | NA | Material | Stainless steel | 0.077061 | NA | NA | NA | NA | 0.17385
Plumbing | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Waste & Vent | NA | Material | Cast iron pipe | 1.3832 | NA | NA | NA | NA | 3.9835
Plumbing | High performance | 20000-300000 | 80000 | Medium | Medium HP b | Waste & Vent | NA | Material | PVC | 0.13504 | NA | NA | NA | NA | 0.43078
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard a | VAV AHU w/ PFP Terminals | NA | Equipment | VAV AHU w/ DX | 1.7341 | 350 | 500 | 12 | 18 | 11.779
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard a | VAV AHU w/ PFP Terminals | NA | Equipment | VAV Terminals w/ electric heat | 0.90539 | 350 | 500 | 12 | 18 | 3.7185
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard b | WSHP | NA | Equipment | Cooling tower | 2.0748 | 350 | 500 | 12 | 18 | 10.3458
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard b | WSHP | NA | Equipment | Boiler | 0.40916 | 350 | 500 | 12 | 18 | 4.9721
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard b | WSHP | NA | Equipment | Distributed zone WSHP | 1.5782 | 350 | 500 | 12 | 18 | 3.0172
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard b | WSHP | NA | Equipment | Pumps | 0.42597 | 350 | 500 | 12 | 18 | 0.81436
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP a | DOAS + Chilled Beam | NA | Material | Galv sheet metal | 4.2085 | 400 | 600 | 10 | 15 | 10.1004
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP a | DOAS + Chilled Beam | NA | Material | Flexible duct | 0.18094 | 400 | 600 | 10 | 15 | 0.96443
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP a | DOAS + Chilled Beam | NA | Material | Steel pipe | 1.4929 | 400 | 600 | 10 | 15 | 3.3679
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP a | DOAS + Chilled Beam | NA | Material | Copper pipe | 1.6815 | 400 | 600 | 10 | 15 | 3.6824
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP a | DOAS + Chilled Beam | NA | Material | Insulation - duct wrap | 0.34097 | 400 | 600 | 10 | 15 | 1.9401
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP a | DOAS + Chilled Beam | NA | Material | Insulation - hydronic water insulation | 0.19484 | 400 | 600 | 10 | 15 | 1.2703
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP a | DOAS + Chilled Beam | NA | Material | Refrigerants | 0.019484 | 400 | 600 | 10 | 15 | 36.8245
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP b | DOAS + WSHP | NA | Material | Galv sheet metal | 6.8903 | 400 | 600 | 10 | 15 | 16.5368
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP b | DOAS + WSHP | NA | Material | Flexible duct | 0.18094 | 400 | 600 | 10 | 15 | 0.96443
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP b | DOAS + WSHP | NA | Material | Steel pipe | 1.4771 | 400 | 600 | 10 | 15 | 3.3323
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP b | DOAS + WSHP | NA | Material | Copper pipe | 0.82884 | 400 | 600 | 10 | 15 | 1.8152
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP b | DOAS + WSHP | NA | Material | Insulation - duct wrap | 0.34097 | 400 | 600 | 10 | 15 | 1.9401
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP b | DOAS + WSHP | NA | Material | Insulation - hydronic water insulation | 0.19484 | 400 | 600 | 10 | 15 | 1.2703
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP b | DOAS + WSHP | NA | Material | Refrigerants | 0.019484 | 400 | 600 | 10 | 15 | 36.8245
Mechanical | High performance | 20000-300000 | 80000 | Medium | Medium HP b | DOAS + WSHP | NA | Equipment | Pumps | 0.64358 | 400 | 600 | 10 | 15 | 1.2304
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP a | DOAS + Chilled Beam | NA | Equipment | DOAS w/ heat recovery | 2.2406 | 400 | 600 | 10 | 15 | 8.5775
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP a | DOAS + Chilled Beam | NA | Equipment | Single duct VAVs or CAVs | 0.86703 | 400 | 600 | 10 | 15 | 3.5609
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP a | DOAS + Chilled Beam | NA | Equipment | Boiler | 0.40916 | 400 | 600 | 10 | 15 | 4.9721
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP a | DOAS + Chilled Beam | NA | Equipment | Air Cooled Chiller or Water Cooled Chiller + Cooling tower | 2.3245 | 400 | 600 | 10 | 15 | 20.6362
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP a | DOAS + Chilled Beam | NA | Equipment | Pumps | 0.49026 | 400 | 600 | 10 | 15 | 0.93729
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP b | DOAS + WSHP | NA | Equipment | DOAS w/ heat recovery | 2.2406 | 400 | 600 | 10 | 15 | 8.5775
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP b | DOAS + WSHP | NA | Equipment | Single duct VAVs or CAVs | 0.86703 | 400 | 600 | 10 | 15 | 3.5609
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP b | DOAS + WSHP | NA | Equipment | Cooling tower | 1.8995 | 400 | 600 | 10 | 15 | 9.4715
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP b | DOAS + WSHP | NA | Equipment | Boiler | 0.35071 | 400 | 600 | 10 | 15 | 4.2618
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP b | DOAS + WSHP | NA | Equipment | Distributed zone WSHP | 1.5782 | 400 | 600 | 10 | 15 | 3.0172
Mechanical | High performance | 120000-800000 | 260000 | Large | Large HP b | DOAS + WSHP | NA | Equipment | Pumps | 0.97419 | 400 | 600 | 10 | 15 | 1.8625
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard a | VAV AHU w/ PFP Terminals | NA | Material | Galv sheet metal | 6.6507 | 350 | 500 | 12 | 18 | 15.9617
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard a | VAV AHU w/ PFP Terminals | NA | Material | Flexible duct | 0.17109 | 350 | 500 | 12 | 18 | 0.91192
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard a | VAV AHU w/ PFP Terminals | NA | Material | Insulation - duct wrap | 0.34097 | 350 | 500 | 12 | 18 | 1.9401
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard a | VAV AHU w/ PFP Terminals | NA | Material | Insulation - hydronic water insulation | 0.19484 | 350 | 500 | 12 | 18 | 1.2703
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard a | VAV AHU w/ PFP Terminals | NA | Material | Refrigerants | 0.019484 | 350 | 500 | 12 | 18 | 36.8245
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard b | WSHP | NA | Material | Galv sheet metal | 5.8452 | 350 | 500 | 12 | 18 | 14.0285
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard b | WSHP | NA | Material | Flexible duct | 0.16902 | 350 | 500 | 12 | 18 | 0.90089
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard b | WSHP | NA | Material | Steel pipe | 1.1868 | 350 | 500 | 12 | 18 | 2.6774
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard b | WSHP | NA | Material | Copper pipe | 0.79567 | 350 | 500 | 12 | 18 | 1.7425
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard b | WSHP | NA | Material | Insulation - duct wrap | 0.34097 | 350 | 500 | 12 | 18 | 1.9401
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard b | WSHP | NA | Material | Insulation - hydronic water insulation | 0.19484 | 350 | 500 | 12 | 18 | 1.2703
Mechanical | Standard | 120000-800000 | 260000 | Large | Large Standard b | WSHP | NA | Material | Refrigerants | 0.019484 | 350 | 500 | 12 | 18 | 36.8245
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | In building utility transformer vault and oil filled transformers | Equipment | Transformer vault | 0.27992 | NA | NA | NA | NA | 0.14503
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | Backup generator for life safety systems 500kw diesel | Equipment | Backup Generator | 0.17559 | NA | NA | NA | NA | 0.090975
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | Code minimum time clock controlled lighting system ( Occupancy Sensors in offices) | Equipment | Code minimum time clock, 0.68 lbs/EA | 1.7064 | NA | NA | NA | NA | 0.14728
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | Code minimum time clock controlled lighting system ( Occupancy Sensors in offices) | Material | MC Cable (metallic cable) | 0.67841 | NA | NA | NA | NA | 0.058554
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | LED Lighting | Equipment | LED fixtures | 0.58452 | NA | NA | NA | NA | 6.605
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | LED Lighting | Material | Metal boxes | 0.072594 | NA | NA | NA | NA | 0.0062656
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | Daylight Sensors | Equipment | Daylight sensors | 0.0040916 | NA | NA | NA | NA | 0.018412
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | 4000A Service Distribution | Material | Aluminum feeders 100amp and over | 0.21408 | NA | NA | NA | NA | 0.018477
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | 2000 amp aluminum bus duct riser | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | VFD | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | Sub-metering | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | DATA/AV/Access CNTRL | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | DAS - emergency responder radio only | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard a | Commercial LTG/PWR | FA | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | In building utility transformer vault and oil filled transformers | Equipment | Transformer vault | 0.27992 | NA | NA | NA | NA | 0.14503
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | Backup generator for life safety systems 500kw diesel | Equipment | Backup Generator | 0.17559 | NA | NA | NA | NA | 0.090975
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | Code minimum time clock controlled lighting system ( Occupancy Sensors in offices) | Equipment | Code minimum time clock, 0.68 lbs/EA | 1.7064 | NA | NA | NA | NA | 0.14728
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | Code minimum time clock controlled lighting system ( Occupancy Sensors in offices) | Material | MC Cable (metallic cable) | 0.67841 | NA | NA | NA | NA | 0.058554
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | LED Lighting | Equipment | LED fixtures | 0.58452 | NA | NA | NA | NA | 6.605
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | LED Lighting | Material | Metal boxes | 0.072594 | NA | NA | NA | NA | 0.0062656
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | Daylight Sensors | Equipment | Daylight sensors | 0.0040916 | NA | NA | NA | NA | 0.018412
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | 4000A Service Distribution | Material | Aluminum feeders 100amp and over | 0.21408 | NA | NA | NA | NA | 0.018477
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | 2000 amp aluminum bus duct riser | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | VFD | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | Sub-metering | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | DATA/AV/Access CNTRL | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | DAS - emergency responder radio only | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | Standard | 120000-800000 | 260000 | Large | Large Standard b | Commercial LTG/PWR | FA | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | In building utility transformer vault and oil filled transformers | Equipment | Transformer vault | 0.25428 | NA | NA | NA | NA | 0.13174
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | Backup generator for life safety and optional standby systems 1200kw diesel | Equipment | Backup generator | 0.35106 | NA | NA | NA | NA | 0.18189
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming, addressable fixtures) | Equipment | Occupancy sensors | 0.00076544 | NA | NA | NA | NA | 0.0034445
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming, addressable fixtures) | Material | MC Cable (metallic cable) | 0.33693 | NA | NA | NA | NA | 0.029081
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | LED Lighting | Equipment | LED fixtures | 0.58452 | NA | NA | NA | NA | 6.605
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | LED Lighting | Material | Metal boxes | 0.049829 | NA | NA | NA | NA | 0.0043008
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | Daylight Sensors | Equipment | Daylight sensors | 0.0011817 | NA | NA | NA | NA | 0.0053176
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | 6000A Service Distribution | Material | Copper feeders | 0.33815 | NA | NA | NA | NA | 0.029186
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | 4000A copper bus duct riser | Material | EMT conduit | 0.57131 | NA | NA | NA | NA | 1.6111
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | Energy meters for branch circuit monitoring by system | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | Sub-Metering | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | PV (10000w Solar) | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | DATA/AV/Access CNTRL | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | DAS - Cellular and emergency radio | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | FA | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | PV (10000w Solar) | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP a | Commercial LTG/PWR | VFD | NA | NA | 0 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | In building utility transformer vault and oil filled transformers | Equipment | Transformer vault | 0.25428 | NA | NA | NA | NA | 0.13174
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | Backup generator for life safety and optional standby systems 1200kw diesel | Equipment | Backup generator | 0.35106 | NA | NA | NA | NA | 0.18189
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming, addressable fixtures) | Equipment | Occupancy sensors | 0.00076544 | NA | NA | NA | NA | 0.0034445
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | Enhanced lighting controls (Occupancy Sensors, network controlled relay panels, dimming, addressable fixtures) | Material | MC Cable (metallic cable) | 0.33693 | NA | NA | NA | NA | 0.029081
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | LED Lighting | Equipment | LED fixtures | 0.58452 | NA | NA | NA | NA | 6.605
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | LED Lighting | Material | Metal boxes | 0.049829 | NA | NA | NA | NA | 0.0043008
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | Daylight Sensors | Equipment | Daylight sensors | 0.0011817 | NA | NA | NA | NA | 0.0053176
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | 6000A Service Distribution | Material | Copper feeders | 0.33815 | NA | NA | NA | NA | 0.029186
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | 4000A copper bus duct riser | Material | EMT conduit | 0.57131 | NA | NA | NA | NA | 1.6111
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | Energy meters for branch circuit monitoring by system | NA | NA | 0.0016561 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | Sub-Metering | NA | NA | 0.0016561 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | PV (10000w Solar) | NA | NA | 0.0016561 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | DATA/AV/Access CNTRL | NA | NA | 0.0016561 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | DAS - Cellular and emergency radio | NA | NA | 0.0016561 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | FA | NA | NA | 0.0016561 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | PV (10000w Solar) | NA | NA | 0.0016561 | NA | NA | NA | NA | 0
Electrical | High performance | 120000-800000 | 260000 | Large | Large HP b | Commercial LTG/PWR | VFD | NA | NA | 0.0016561 | NA | NA | NA | NA | 0
Plumbing | Standard | 120000-800000 | 260000 | Large | Large Standard a | Water | NA | Material | Copper pipe | 0.80342 | NA | NA | NA | NA | 1.7595
Plumbing | Standard | 120000-800000 | 260000 | Large | Large Standard a | Water | NA | Material | Stainless steel | 0.06732 | NA | NA | NA | NA | 0.15187
Plumbing | Standard | 120000-800000 | 260000 | Large | Large Standard a | Waste & Vent | NA | Material | Cast iron pipe | 1.3625 | NA | NA | NA | NA | 3.9239
Plumbing | Standard | 120000-800000 | 260000 | Large | Large Standard a | Waste & Vent | NA | Material | PVC | 0.12469 | NA | NA | NA | NA | 0.39776
Plumbing | Standard | 120000-800000 | 260000 | Large | Large Standard b | Water | NA | Material | Copper pipe | 0.80342 | NA | NA | NA | NA | 1.7595
Plumbing | Standard | 120000-800000 | 260000 | Large | Large Standard b | Water | NA | Material | Stainless steel | 0.06732 | NA | NA | NA | NA | 0.15187
Plumbing | Standard | 120000-800000 | 260000 | Large | Large Standard b | Waste & Vent | NA | Material | Cast iron pipe | 1.3625 | NA | NA | NA | NA | 3.9239
Plumbing | Standard | 120000-800000 | 260000 | Large | Large Standard b | Waste & Vent | NA | Material | PVC | 0.12469 | NA | NA | NA | NA | 0.39776
Plumbing | High performance | 120000-800000 | 260000 | Large | Large HP a | Water | NA | Material | Copper pipe | 0.80342 | NA | NA | NA | NA | 1.7595
Plumbing | High performance | 120000-800000 | 260000 | Large | Large HP a | Water | NA | Material | Stainless steel | 0.06732 | NA | NA | NA | NA | 0.15187
Plumbing | High performance | 120000-800000 | 260000 | Large | Large HP a | Waste & Vent | NA | Material | Cast iron pipe | 1.3625 | NA | NA | NA | NA | 3.9239
Plumbing | High performance | 120000-800000 | 260000 | Large | Large HP a | Waste & Vent | NA | Material | PVC | 0.12469 | NA | NA | NA | NA | 0.39776
Plumbing | High performance | 120000-800000 | 260000 | Large | Large HP b | Water | NA | Material | Copper pipe | 0.80342 | NA | NA | NA | NA | 1.7595
Plumbing | High performance | 120000-800000 | 260000 | Large | Large HP b | Water | NA | Material | Stainless steel | 0.06732 | NA | NA | NA | NA | 0.15187
Plumbing | High performance | 120000-800000 | 260000 | Large | Large HP b | Waste & Vent | NA | Material | Cast iron pipe | 1.3625 | NA | NA | NA | NA | 3.9239
Plumbing | High performance | 120000-800000 | 260000 | Large | Large HP b | Waste & Vent | NA | Material | PVC | 0.12469 | NA | NA | NA | NA | 0.39776
[10 empty] | 8.0996 |  |  |  |  | 38.684

## Results Quantities_MEP
Material Quantities [kg/m2]
(empty) |  | Category
Building type | Building model | Electrical | Mechanical | Plumbing | Total Result
Standard
Large Standard a
Large Standard b
Medium Standard a
Medium Standard b
Small Standard a
Small Standard b
XSmall Standard a
XSmall Standard b
High performance
Large HP a
Large HP b
Medium HP a
Medium HP b
Small HP a
Small HP b
XSmall HP a
XSmall HP b
Total Result

## Results Quantities_HVAC
Category | Mechanical
(empty) |  | Item name
Building type | Building model | Air Cooled Chiller or Water Cooled Chiller + Cooling tower | Boiler | Cooling tower | Copper pipe | Distributed zone WSHP | DOAS ERV w/ electric heat | DOAS w/ heat recovery | Flexible duct | Galv sheet metal | Insulation - hydronic water insulation | Packaged units | Pumps | Refrigerants | Single duct VAVs or CAVs | Steel pipe | VAV AHU w/ DX | VAV Terminals w/ electric heat | VRF casettes | VRF fan coils | VRF outdoor units | Insulation - duct wrap | Total Result
Standard
Large Standard a
Large Standard b
Medium Standard a
Medium Standard b
Small Standard a
Small Standard b
XSmall Standard a
XSmall Standard b
High performance
Large HP a
Large HP b
Medium HP a
Medium HP b
Small HP a
Small HP b
XSmall HP a
XSmall HP b
Total Result

## Results Quantities_ELEC
Category | Electrical
(empty) |  | Item name
Building type | Building model | Aluminum feeders 100amp and over | Backup Generator | Basic Service Switchgear | Battery | Copper feeders | DATA/AV/Access CNTRL | EMT conduit | FA | Feeder Wire | Fixtures | LED fixtures | MC Cable (metallic cable) | NA | Non-metallic boxes | Non-Metallic Cable | Transformer | Transformer vault | Total Result
Standard
Large Standard a
Large Standard b
Medium Standard a
Medium Standard b
Small Standard a
Small Standard b
XSmall Standard a
XSmall Standard b
High performance
Large HP a
Large HP b
Medium HP a
Medium HP b
Small HP a
Small HP b
XSmall HP a
XSmall HP b
Total Result

## Results Quantities_PLUMB
Category | Plumbing
(empty) |  | Item name
Building type | Building model | Copper pipe | PVC | Stainless steel | PEX water pipe | Cast iron pipe | Total Result
Standard
Large Standard a
Large Standard b
Medium Standard a
Medium Standard b
Small Standard a
Small Standard b
XSmall Standard a
XSmall Standard b
High performance
Large HP a
Large HP b
Medium HP a
Medium HP b
Small HP a
Small HP b
XSmall HP a
XSmall HP b
Total Result

## Results LCA_MEP
Item name | - multiple -
(empty) |  | Category
Building type | Building model | Electrical | Mechanical | Plumbing | Total Result
Standard
Large Standard a
Large Standard b
Medium Standard a
Medium Standard b
Small Standard a
Small Standard b
XSmall Standard a
XSmall Standard b
High performance
Large HP a
Large HP b
Medium HP a
Medium HP b
Small HP a
Small HP b
XSmall HP a
XSmall HP b
Total Result

## Results LCA_HVAC
Category | Mechanical
(empty) | Item name
Building model | Air Cooled Chiller or Water Cooled Chiller + Cooling tower | Boiler | Cooling tower | Copper pipe | Distributed zone WSHP | DOAS ERV w/ electric heat | DOAS w/ heat recovery | Flexible duct | Galv sheet metal | Insulation - hydronic water insulation | Packaged units | Pumps | Single duct VAVs or CAVs | Steel pipe | VAV AHU w/ DX | VAV Terminals w/ electric heat | VRF casettes | VRF fan coils | VRF outdoor units | Insulation - duct wrap | Total Result
Large HP a
Large HP b
Large Standard a
Large Standard b
Medium HP a
Medium HP b
Medium Standard a
Medium Standard b
Small HP a
Small HP b
Small Standard a
Small Standard b
XSmall HP a
XSmall HP b
XSmall Standard a
XSmall Standard b
Total Result

## Results LCA_ELEC
Category | Electrical
(empty) |  | Item name
Building type | Building model | Aluminum feeders 100amp and over | Backup Generator | Basic Service Switchgear | Battery | Copper feeders | DATA/AV/Access CNTRL | EMT conduit | FA | Feeder Wire | Fixtures | LED fixtures | MC Cable (metallic cable) | NA | Non-metallic boxes | Non-Metallic Cable | Transformer | Transformer vault | (empty) | Battery 20W unit | Metal boxes | Daylight sensors | Occupancy sensors | Data/WAP (Wireless) | D-Rings 0.15 lbs/EA | Code minimum time clock, 0.68 lbs/EA | Energy meters, 0.59 lbs/EA | Total Result
High performance
Large HP a
| Large HP b | [27 empty] | 17.2021
| Medium HP a | [27 empty] | 17.6712
| Medium HP b | [27 empty] | 17.9456
| Small HP a | [27 empty] | 31.8621
Small HP b
XSmall HP a
XSmall HP b
Standard
Large Standard a
Large Standard b
Medium Standard a
Medium Standard b
Small Standard a
Small Standard b
XSmall Standard a
XSmall Standard b
Total Result

## Results LCA_PLUM
Category | Plumbing
(empty) |  |  | Item name
Building type | System type | Building Size Category | Cast iron pipe | Copper pipe | PEX water pipe | PVC | Stainless steel | Total Result
High performance
Waste & Vent
Large
Medium
Small
XSmall
Water
Large
Medium
Small
XSmall
Standard
Waste & Vent
Large
Medium
Small
XSmall
Water
Large
Medium
Small
XSmall
Total Result